Emergency Response Plan (ERP) for

Bayview Water & Sewer (ID1280014)     (October 2020-October 2025)

REVIEW AND UPDATE ANNUALLY*

| Date Reviewed | Reviewed By | Comments (Attach Additional Document as Needed) |
| --- | --- | --- |
| Dec 2020 |  |  |
| June 2021 |  |  |
| Dec 2021 |  |  |
| June 2022 |  |  |
| Dec 2022 |  |  |
| June 2023 |  |  |
| Dec 2023 |  |  |
| June 2024 |  |  |
| Dec 2024 |  |  |
| Oct 2025 |  |  |

Contents

Emergency Response Plan Requirements	3

Section 1. System Information	4

Section 2. Chain of Command – Lines of Authority	6

Section 3. Events that Cause Emergencies	7

Section 4. Emergency Notification	8

Section 5. Effective Communication	14

Section 6. Response Actions for Specific Events	15

Section 7 Alternate Water Sources	20

Section 8. Returning to Normal Operation	23

Section 9. Future Planning	24

Section 10. Plan Approval	25

Tables

Table 1. System Information………………………………………………………………………………...4

Table 2. Chain of Command…………………………………………………………………………………6

Table 3. First Responders of an Emergency……………………………………………………………..8

Table 4. Prioritizing water use during Restrictions and Emergencies……………………………..21

Emergency Response Plan Requirements

INTRODUCTION:

The Emergency Response Plan is a blueprint outlining roles and responsibilities in the event that the water system experiences a disruption due to contamination, loss of power, natural disasters such as drought or flooding, or other circumstances where it cannot provide services. The plan helps local officials make decisions under the most adverse conditions. Development and implementation of this contingency plan increases the likelihood that correct and immediate action will be taken and that any damage or potential health risk, both in the short and long term, will be minimized.

Regardless of protection strategies and efforts to prevent contamination or exposure of the municipal water system to harmful materials, it is recognized that contamination may still occur either from accidental chemical releases, intentional acts of vandalism, or as unforeseen results of the otherwise legal use of hazardous materials.

This Plan is developed on the premise that electrical or mechanical failure is the most likely threat to the drinking water system. However, the provisions of the plan may be employed in any event that poses a threat to the municipal drinking water system. If deemed of sufficient severity, the town of Santa may declare a state of emergency or disaster under the provisions of the Idaho Code Chapter 10, title 46, Idaho Emergency Preparedness Act in order to request resources and support assistance from Benewah County, the state of Idaho, and/or federal agency sources.

This Plan addresses emergency contact lists, potential risks and how to address them, alternate sources of safe drinking water along with calculated water demands for the present and the future. This plan contains the necessary guidelines for public notice and instructions for protection of public health during a short- or long-range emergency.

This separate Plan for Bayview W&S, satisfies the Emergency Response requirements for Bayview Source Water Protection Plan (SWPP), to be implemented (Oct 2020 – Oct 2025).

This plan will be in effect until 9/31/2025 and reviewed bi-annually (June and December)

Section 1.
System Information

Keep this basic information easily accessible to authorized staff for emergency responders, repair people, and the news media.

Table 1. System information

| System Identification Number | Bayview Water & Sewer ID1280014 |  |  |
| --- | --- | --- | --- |
| System Name and Address | Bayview Water and Sewer District. Bayview, Idaho 83803 |  |  |
| Directions to the System | North on Hwy 95 from Coeur d’ Alene to Athol then east to Bayview |  |  |
| Basic Description and Location of System Facilities | Records at Bayview Water & Sewer District Location Two wells #7 and #8 with 4 Storage Tanks |  |  |
| Location/Town | System Office: 16401 East Emerson in Bayview, Idaho * Muster Location in case of an emergency Office Phone: (208) 683-3948 |  |  |
| Population Served and Service Connections from Division of Drinking Water Records | 1258 people | 466 connections |  |
| System Owner | Bayview Water & Sewer |  |  |
| Name, Title, and Phone Number of Person Responsible for Maintaining and Implementing the Emergency Plan | Robert Kuchenski (Operator) - Ali Spahn (Planning Team) - Jessie Roe – Treasurer - Bwsd637@gmail.com (jroe.pas@hotmail.com Calvin Nolan_W&S Chairman- Ted Bare - |  | (208)-683-3949 (559) 776-1776 (208) 683-3948 (208) 683-3948 or (208)755-1588 (208) 683-7018 |

Bayview Emergency Action Plan

- Notify Chain of Command listed in section 2 on page 6 of this document.

a. Notify appropriate local, State and/or Federal Agencies- (Pages 8, 9)

b. Notify appropriate news and/or media sources -media contact list- (page 10)

c. Notify Customers- (Methods on page 12)

- Was this situation deliberate, accidental or unplanned?

(If deliberate does law enforcement need to be notified)?

- Assess damage to system, determine need to isolate or shut down system.

  - Is there sufficient water for drinking and irrigation?

  - Does sufficient backup capacity and transmission exist?

- Repair damage or bring on redundant sources of drinking water (See Haulers)

- Return system to safe operation

- Notify appropriate authorities that system is safe and is back in operation.

Section 2.
Chain of Command – Lines of Authority

The first response step in any emergency is to inform the person at the top of this list, who is responsible for managing the emergency and making key decisions.

Table 2. Chain of command – lines of authority

| Name and Title | Responsibilities During an Emergency | Contact Numbers |
| --- | --- | --- |
| Robert Kuchenski - (Operator)-SWP Team Leader | To identify the emergency, access the emergency, contact employees, and Board Chair as needed bob@itegritywater.net | (208) 683-3949 |
| Bob Hansen Alternate Operator | To identify the emergency, access the emergency, contact employees, and Board Chair as needed | (208) 265-4270 |
| Jessie Roe | Support help for the operators, contact area agencies, contact board members as needed. Contact needed professionals as directed by operators. Notify media- bwsd637@gmail.com | (208) 683-3948 |
| Calvin Nolan | District Chair Person-bullseyenid@yahoo.com | (208) 755-1598 |
| Ali Spahn | SWP Team Member - alispahn@yahoo.com> | (559) 776-1776 |
| Larry Leake | SWP Team Member- larry.m.leake@hotmail.com> | (928) 210-0008 |
| Ted Bare | Board member & SWP Team Member 3bareted@gmail.com> | (208) 683-7018 |
| Bob Kuchenski | Water Operator & Incident Commander | (208) 683-3949 |

External Chain of Command

| Andy Olson | Drink Water Compliance | (208) 666-4630 | Andy.Olson@deq.idaho.gov |
| --- | --- | --- | --- |
| Anna Moody | Drinking Water Supervisor | (208) 666-4612 (208) 699-8260 Cell | Anna.Moody@deq.idaho.gov |
| John Jose | Source Water Protection | (208) 666-4620 | John.Jose@deq.idaho.gov |
| Matt Plaisted | IDEQ Engineering Manager | (208) 666-4629 | Matt.Plaisted@deq.idaho.gov |
| Kyle Meschko | District Engineer | (208) 813-7603 | kmeschko@Kellerassociates.com |

Section 3.
Events that Cause Emergencies

The events listed below may cause water system emergencies. They are arranged from highest to lowest probable risk.

Events that cause emergencies

| Type of Event | Probability or Risk (High-Med-Low) | Comments |
| --- | --- | --- |
| High Winds resulting in power outage | High | Wind storms in the spring and fall generate winds in excess of 50 miles an hour or often greater. These storms can disrupt power from time to time. |
| Human-caused events | Medium | Construction excavation in the area could damage underground main lines. |
| Forest Fires | Medium | Forest fires could devastate our watershed. However, the entire watershed has recently been clear-cut, so this threat is not likely in the near future. |
| Loss of electrical power for various reasons | Medium | Back-up Generators at most locations….Well #7 has manual transfer |

Section 4.
Emergency Notification

Table 3. Notification call-up lists - Use these lists to notify first responders of an emergency.

| Emergency Notification List |  |  |  |  |
| --- | --- | --- | --- | --- |
| Organization or Department | Name & Position | Telephone | Night or Cell Phone | Email |
| Local Law Enforcement |  |  | 911 |  |
| Fire Department | Timberlake Fire Department | 208-683-3333 | 911 |  |
| Idaho Emergency Alert System |  |  | 1-888-225-5322 |  |
| State Communications |  | 1-800- 632-8000 | 1-800- 632-8000 |  |
| Emergency Medical Services | Timberlake Fire Department | 911 | 911 |  |
| Hazmat Hotline |  | 1-800-632-8000 |  |  |
| National Poison Control Center |  | 1-800-222-1222 |  |  |
| Farragut State Park (no physical connection) | Farragut State Park | 208-683-2975 |  |  |
| Bureau of Hazardous Materials |  | 208-422-5726 |  |  |
| NOAA Hazmat Response |  | 7-206-526-4911 |  |  |
| Bureau of Environmental Health and Safety |  | 208-334-2584 |  |  |
| Idaho State Alert Warning System | (ISAWS) | 208-258-6595 |  |  |

| Priority Customers |  |  |  |  |
| --- | --- | --- | --- | --- |
| Organization or Department | Name & Position | Telephone | Night or Cell Phone | Email |
| Senic Bay Marina | Kristen Morgan | 208-683-2243 |  |  |
| US Naval Acoustic Research CTR | Alan Griffiths | (208)683-2321 |  |  |
| Hudson Bay Resort | Gary McDonald | (208)-683-2211 |  |  |

| State, Federal Notification List |  |  |  |  |
| --- | --- | --- | --- | --- |
| Organization or Department | Name & Position | Telephone | Night/Cell phone | Email |
| 1) Neighboring Water System (not connected) | Dennis Woolford (Farragut) | (208) 683-2975 |  |  |
| State Police | ID State Police | 208-209-8620 | 208-209-8730 |  |
| Sheriff’s Office- | Kootenai County Sheriff | 208-446-1300 |  |  |
| Authorized Testing Laboratory | Accurate Testing Lab | 208-762-8378 |  |  |
| Regional DEQ contact | Anna Moody | 208-769-1422 | 208-699-8260 | Anna.Moody@deq.idaho.gov |
| Regional DEQ Contact | IDEQ Andy Olson | 208-666-4630 | 208-666-4630 | Andy.Olson@deq.idaho.gov |
| Regional DEQ Contact | John Jose | 208-666-4620 |  | John.Jose@deq.idaho.gov |
| Idaho DEQ | State Office | 208-343-0502 |  |  |
| U.S. EPA Region 10 Spill Response |  | 206-553-1263 |  |  |
| Idaho Transportation Department | Kootenai County DOT | 208-772-1200 |  | Itd.idaho.gov |
| Regional Health Department | Panhandle Health District | 208-415-5100 |  |  |
| RCAC Contact | Jim Wilson | 509-927-6748 | 509-590-7310 | jwilson@rcac.org |
| Idaho Rural Water Contact | Gary Sievers | 208-343-7001 | 208-530-3115 | gsievers@idahoruralwater.com |
| Idaho State Communication |  | 1-800-632-8000 |  |  |
| Organization or Department | Name & Position | Telephone | Night or Cell No. | Email |
| National Weather Service | Idaho | 208-334-6860 |  |  |
| Safe Drinking Water Hotline |  | 800-426-4791 |  |  |

| Service / Repair Notifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| BAYVIEW WEB SITE: Bayviewwaterandsewer.com |  |  |  |  |
| Organization or Department | Name & Position | Telephone | Night or Cell Phone | Email |
| Electrician- (One option) | Bigfoot Tech | 208-981-0304 |  |  |
| Pump Supplier | RC Worst | 208-664-2133 |  |  |
| “Call Before You Dig” | Get info before dig | 811 |  |  |
| Rental Equipment Supplier | 40 Rentals Store | 208-762-3998 |  |  |
| Chlorine Supplier | OX-ARC | 208-765-3311 |  |  |
| Pipe Supplier | Consolidated Supply | 208-762-2568 |  |  |
| 1) Water Truck | Standish Water Trucks | 208- 687-1315 | 208-699-1943 | Tank truck delivery-3,000-gal |
| 1) Water Supplier | Culligan Water Filtration | 208-664-3216 |  | Have 5-gal water containers |
| 2) Water Supplier | Clearwater Springs | 208-762-2370 |  | Have 1 & 5-gal water containers |

Media-Communications

| Organization or Department | Name & Position | Telephone | Email |
| --- | --- | --- | --- |
| 1) Newspaper – Regional | #### The CDA Press | #### 208) 664-8176 | mpatrick@cdapress.com bbuley@cdapress.com |
| 2) Newspaper – Regional | #### The Spokesman Review_ | #### (509)-459-5400 | news@spokesman.com |
| Radio FM | #### KHTQ - 94.5 | #### (509) 324-4000 |  |
| “ | #### KPND – 95.3 | #### (208) 263-2179 |  |
| “ | #### KCDA –103.1 | #### (509) 242-2400 |  |
| “ | #### KICR – 102.3 | #### (208) 664-3241 |  |
| “ | #### KDRK – 93.7 | #### (509) 241-0937 |  |
| “ | #### KIXZ – 96.1 | #### (509) 242-2400 |  |
| “ | #### KMBI – 107.9 | #### (509) 448-2555 |  |
| Organization or Department | Name & Position | Telephone | Email |
| “ | #### KPBX – 91.1 | #### (509) 328-5729 |  |
| “ | #### KXLY – 96.9 | #### (509) 324-4000 |  |
| “ | #### KZZU – 92.9 | #### (509) 324-4000 |  |
| “ | #### KISC – 98.1 | #### (509) 242-2400 |  |
| “ | #### KEYF – 101.1 | #### (509) 448-3968 |  |
| “ | #### KZBD – 105.7 | #### (509) 448-1000 |  |
| “ | #### KKZX – 98.9 | #### (509) 241-5599 |  |
| “ | #### KSFC – 91.9 | #### (509) 328-5729 |  |
| “ | #### KEEH – 104.9 | #### (509) 344-5757 |  |
| “ | #### KYWL – 103.9 | #### (509) 448-1000 |  |
| “ | #### KEWU – 89.5 | #### (509) 359-6390 |  |
| “ | #### KAGU – 88.7 | #### (509) 328-4220 |  |
| “ | #### KEZE – 99.9 | #### (509) 324-4000 |  |

| Organization or Department | Name & Position | Telephone | Email |
| --- | --- | --- | --- |
| Radio AM | #### KVNI – 1080 | #### (208) 664-9271 |  |
|  | #### KGA – 1510 | #### (509) 448-7874 |  |
|  | #### KXLY – 920 | #### (509) 324-4000 |  |
|  | #### KXLX – 700 | #### (509) 324-4000 |  |
|  | #### KQNT – 590 | #### (509) 242-2400 |  |
|  | #### KJRB – 790 | #### (509) 279-7000 |  |
|  | #### KEYF – 1050 | #### (509) 232-1011 |  |
|  | #### KZFS- 1280 | #### (509) 242-2400 |  |
|  | #### KTRW – 970 | #### (509) 443-1000 |  |
| TV Station | KHQ Channel 6 KREM Channel 2 KXLY Channel 4 KSPS Channel 7 KAYU Channel 28 | #### (509) 667-2326 (509) 448-2000 509) 768-4004 (509) 443-7800 (509) 448-2828 | #### khqnewsdesk@khq.com newsdesk@krem.com news4@kxly.com |

IDAHO EMERGENCY ALERT SYSTEM:

For immediate public health and safety- via AM and FM radio, Broadcast TV, Cable TV, Land Mobile Radio Service, VHF, UHF and FiOS wireless, Digital TV, Satellite TV, Digital Cable, Sirius SM Satellite Radio, IBOC, Smart phones and  Direct and Dish TV Networks.

- All LOCAL Broadcast Media-(National public Warning System requires all media to provide communications during a national emergency).

- Automatically included via EAS Activation…………1-888-225-5322

- https://www.fcc.gov/general/emergency-alert-system-eas

| Notification: | -Phone list or door to door notification. |
| --- | --- |
|  | Facebook and Website |

-Additional methods of emergency alert:

*Shorelines: e-mail: sherylpp@gmail.com

*Bylines: e-mail: jyesca6@gmail.com

Alert local law enforcement, state and federal drinking water officials, and local health agencies

| Who is Responsible: | Robert Kuchenski (Operator) (SWP Team leader) Ali Spahn – (SWP Team Member) Calvin Nolan – (District Chair Person) Jessie Roe – Bayview W&S (Treasurer) Ted Bare – SWP Team Member *Any of the board members available can contact officials |
| --- | --- |
| Procedures: | Call, give information as specified by operator |

Contact service and repair contractors

| Who is Responsible: | Robert Kuchenski (Operator) (SWP Team leader) Ali Spahn – (SWP Team Member) Jessie Roe – Bayview W&S (Treasurer) Ted Bare-(SWP Team Member |
| --- | --- |
| Procedures: | Call, give information as specified by operator |

Contact neighboring water systems, if necessary

| Who is Responsible: | Robert Kuchenski (Operator) (SWP Team leader) Ali Spahn – (SWP Team Member) Jessie Roe – Bayview W&S (Treasurer) |
| --- | --- |
| Procedures: | Bayview W&S to contact Farragut State Park (208) 683-2975 |

Procedures for issuing a health advisory - (Loss of water pressure – 24 hrs max)

| Who is Responsible: | Robert Kuchenski (Operator) (SWP Team leader) Ali Spahn – (SWP Team Member) Calvin Nolan – (District Chair Person) Jessie Roe – Bayview W&S (Treasurer) Ted Bare-(SWP Team Member) |
| --- | --- |
| Procedures: | Call, give information as specified by operator and / or IDEQ. Neighboring systems for backup would be Farragut State Park |

Distribution of Public Notification

| Who is Responsible: | Robert Kuchenski (Operator) Calvin Nolan – District Chair Person Jessie Row – Treasure Ted Bare-(SWP Team Member Any board member can call and give emergency information as specified by the water operator |
| --- | --- |

Section 5.
Effective Communication

Communication with customers, the news media, and the general public is a critical part of emergency response.

Designated public spokesperson

Designate a spokesperson (and alternate) and contact your local primacy agency for delivering messages to the news media and the public.

Designate a spokesperson and alternates

| Spokesperson | Alternate |
| --- | --- |
| Bob Kuchenski- (208)683-3949 | Bob Hansen-(208) 265-4270 |
| Calvin Nolan-(208)755-1598 | Ali Spahn-(208) 561-5232 or Ted Bare- (208) 683-7018 |

Health advisories: During events when water quality and human health are in question, it may be necessary to issue a health advisory that gives advice or recommendations to water system customers on how to protect their health when drinking water is considered unsafe. These advisories are issued when the health risks to the consumers are sufficient, in the estimation of the water system, state or tribal, or local health officials, to warrant such advice.

Health advisories usually take the form of a drinking water warning or boil water advisory. Communication during these times is critical. Health advisories should always be well thought out and provide very clear messages.

The U.S. Environmental Protection Agency has put together a number of tools, including fact sheets, brochures, forms, and templates to help prepare for a health advisory: *http://www.deq.idaho.gov/water-quality/drinking-water/pws-switchboard.aspx...... *http://www.epa.gov/safewater/pn.html

Section 6.
Response Actions for Specific Events

In any event, there are a series of general steps to take:

- Analyze the type and severity of the emergency;

- Take immediate actions to save lives;

- Take action to reduce injuries and system damage;

- Make repairs based on priority demand, and

- Return the system to normal operation.

The following tables identify the assessment, set forth immediate response actions, define what notifications need to be made, and describe important follow-up actions.

- Power outage

| # Assessment | Determine how widespread, Call local Power Co. ask for timeline |
| --- | --- |
| Immediate Actions | None required, the system is gravity fed from storage reservoirs. We have no booster pumps. Do have a diesel powered generator for emergencies. |
| Notifications | None Required |
| Follow-up Actions | We should have a transfer switch installed at the well house so that the well could be powered by our portable generator. |

- Distribution line break

| # Assessment | Determine location or problem and type of problem |
| --- | --- |
| Immediate Actions | Turn off Valves, to stop flow. Call 811. May have to call excavator. |
| Notifications | IDEQ, Customers |
| Follow-up Actions | Fix the line break, and then flush generously. May need to turn off all affected water meters and hyper chlorinate the pipeline. Take construction samples, and wait for sample results from lab. |

- Chlorine treatment equipment failure

| # Assessment | Determine what has failed, repair, or replace |
| --- | --- |
| Immediate Actions | Isolate the chlorine (Sodium Hypochlorate) equipment |
| Notifications | IDEQ – May have to contact customers |
| Follow-up Actions | If the failure was preventable, take steps to prevent it in the future. |

- Treatment equipment

| # Assessment | Determine what has failed, repair, or replace |
| --- | --- |
| Immediate Actions | Isolate the chlorine equipment from the water system flow |
| Notifications | IDEQ |
| Follow-up Actions | Depends on what has failed, and if it presents a public health threat. |

- Source pump failure

| # Assessment | Turn off well - Use back up well |
| --- | --- |
| Immediate Actions | Isolate---then use back-up system only |
| Notifications | Call pump company- -RC Worst @ (208) 664-2133 |
| Follow-up Actions | Repair as necessary |

- Microbial (coliform, E. coli and Cyanotoxin Formation ) contamination

| # Assessment | Determine if possible the source of contamination |
| --- | --- |
| Immediate Actions | Call IDEQ, flush if advised, increase chlorine immediately. |
| Notifications | IDEQ, follow their instructions |
| Follow-up Actions | Do required follow up testing |

- Chemical contamination

| # Assessment | Determine source of contamination, Type of chemical, may need to evacuate the area. May need to call Timberlake Fire Department and/or Hazmat. |
| --- | --- |
| Immediate Actions | Isolate contamination if possible |
| Notifications | IDEQ, Follow their instructions |
| Follow-up Actions | Depends on the chemical and circumstances. |

- Vandalism or terrorist attack

| # Assessment | Determine extent of damage |
| --- | --- |
| Immediate Actions | Restore Service, Repair if possible |
| Notifications | Sheriff’s Office-(208) 446-1300 |
| Follow-up Actions | Unknown, Depends on the situation |

- Reduction or loss of water in the well

| # Assessment | Determine cause of reduction or loss in a well…. |
| --- | --- |
| Immediate Actions | Consider preparation for a long run time. |
| Notifications | Update customer contact list |
| Follow-up Actions | Contact IDWR, inquire about aquifer changes that they may be aware of |

- Drought

| # Assessment | N/A |
| --- | --- |
| Immediate Actions | None Required |
| Notifications | None Required |
| Follow-up Actions | None Required |

- Flood

| # Assessment | There should be no damage. If there is, determine extent |
| --- | --- |
| Immediate Actions | Depends on what has been damaged. |
| Notifications | Depends on what has been damaged. |
| Follow-up Actions | Depends on what has been damaged. |

- Earthquake

| # Assessment | Determine extent of damage at facilities, well, slow sand filter |
| --- | --- |
| Immediate Actions | Address obvious damage – Repair if possible- Check TOWER |
| Notifications | Kootenai County, IDWARN, IDEQ |
| Follow-up Actions | Expect underground pipeline damage that is not obvious. Monitor for leakage. |

- Hazardous materials spill in vicinity of sources or system lines

| # Assessment | Try to determine where the hazardous materials spill is, determine what it is |
| --- | --- |
| Immediate Actions | Determine the type of hazardous material. The area may have to be evacuated. Timberlake fire carries a book that can be used to identify place cards. Wait for Hazmat Crew. |
| Notifications | IDEQ, Fire, Hazmat, IDEQ, IDWARN and other Personnel |
| Follow-up Actions | Required testing of water |

- Electronic equipment failure

| # Assessment | Troubleshoot, call RC Worst Pump & Co. (208) 684-2133 or Bigfoot Technical (208)981-0304 |
| --- | --- |
| Immediate Actions | Repair as soon as possible |
| Notifications | IDEQ, if it appears to be long term or possibly result in a violation |
| Follow-up Actions | Consider stocking failed parts |

- Cyber attack

| # Assessment | Determine if the water PLC is affected. Determine if office computer is affected. Do not delete any thing |
| --- | --- |
| Immediate Actions | Call ICRMP, follow their instructions |
| Notifications | Work with ICRMP |
| Follow-up Actions | Re-install back up program- Back up computers routinely |

Steps to follow if emergency is affecting the water source:

- The Incident Commander (in this case the main water operator), system engineer and governing board officials will coordinate and serve as liaisons with the Incident Commander to assess threats and implement water system protection measures.

- If not already done by the Incident Commander, the Idaho State Communications Center (State Com) will be notified of the type and properties of the release.                (1-800-632-8000).

- The water operator will initiate system source isolation (e.g. shutting down wells; isolating spring sources, etc.) as determined appropriate for the event.

- Working with the water operator and District Manager, public notifications, water usage restrictions, and priority use protocol will be implemented as necessary.

- The Idaho Department of Environmental Quality (DEQ), District Health Department, and other state and/or federal agency(s) that may be involved will be consulted and coordinated with to ensure the mediation and safety of delivered drinking water.

- If the event makes drinking water unusable, the need to supply supplemental drinking water (bottled water, etc.) will be assessed and determined by the water operator and District Manager.

In keeping with the County Emergency Operations Plan, the County Office of Emergency Management and the Bureau of Disaster Services Area Field Officer (BDSAFO) will be notified. In the event that needed resources are not available within the County, the County Emergency Manager and BDSAFO will work through the State Emergency Operations Center to facilitate resource requests.

Questions to consider during an emergency?

- Is the event ongoing or has it been stopped?

- Do local emergency units have to be called in?

- Are any businesses affected or vulnerable communities (nursing homes, hospitals, etc.) or people with health problems affected?

- Do we need to provide bottled drinking water to customers?

- Do we need to contact Idaho DEQ?

- Has the highway district or Idaho transportation department been contacted?

- Do all staff members understand the problem and their roles and responsibilities?

Section 7.
Alternative Water Sources

Intertie to adjacent water supply system

| Water Systems within One-Quarter Mile of our System | Feasibility of Connecting |
| --- | --- |
| No Public Water System close except Farragut State Park well that could supply water to Bayview in an emergency | No direct connection |

Alternate source(s) of water

| Alternative Sources | Names | Phone | Availability | Is the Water Safe for Drinking? |
| --- | --- | --- | --- | --- |
| Farragut State Park Wells | Dennis Woolford | (208) 683-2975 | However, for only a short time during an emergency | YES |

PRIORITIES FOR USE OF DRINKING WATER DURING WATER SUPPLY EMERGENCIES

During periods of water system emergencies, priorities for use of drinking water may be established depending upon the severity and anticipated duration of the emergency. Those services and uses determined less critical to public health and safety will be suspended for a period to be determined by Bayview Water System.

This Emergence Response Plan is developed to prepare management for an event of a water system emergency and shall not be deemed to contravene the authority of the District’s leadership personnel. It is recognized that the Bayview Water & Sewer District may exercise its authority and impose other restrictive controls based upon the particular event.

Table 4.  Prioritizing Water Use During Restrictions & Emergencies

|  | Use Advisory | Priority Use | Prohibited Use |
| --- | --- | --- | --- |
| Level 1: Minor contaminants – follow Health District recommendations | Follow Health District Recommendations for specific contaminant (i.e. boil order or other treatment) | Drinking Water- yard & other home uses | Follow Health District Recommendations (i.e. boil order or other treatment) for domestic uses No restrictions |
| Level 2: Reduced supply due to source closure or limitation (including drought) | Watering Restriction Notice | Drinking Water Limited yard and other uses | Yard or garden use by scheduled watering hours only |
| Level 3: Reduced supply due to source closure or limitation (including drought) | Water Restriction Notice | Drinking Water | No outside water use |
| Level 4: Serious hazard affecting water source | Bottled Water only Notification of all media outlets | Limited yard and other uses | NO DOMESTIC USE |
| Level 5: Serious environmental and health hazard from source | Bottled Water ONLY No physical contact Notify all media outlets | No Use Allowed | NO USE OR CONTACT |

Normally Available District Equipment.

Well Sounder

Redundant Sources and Generation Capacity –

There is a standby generator at most facilities

No (current) redundant source connected to distribution system- But can connect to Farragut State Park if necessary

Storage Capacity

| System Name | Storage Capacity, in gallons | Days’ worth of water supply for customers (without pumping) |
| --- | --- | --- |
| Main tank | 225,000 gal | 2.4 days |
| 4 smaller tanks | 171,000 gal | 2.7 days |
| Total from all tanks | 396,000 gal | 6.3 days |

*This supply is with no supply for fire suppression or lawn watering and not during peak summer resident season. During peak season, the supply may last 1 or 2 days.

*Calculations from the table are related to the normal usage per person is 50 gal/day, Therefore, for 1258 people the amount needed would be 62,900 gal/day in storage, without any pumping and not during peak summer season.

---------------------------------------------------------------------------------------------------------------

*Supply days do not account for water used for fire suppression or lawn watering. Estimate of days’ worth of supply are estimates based on average use numbers and assume water restrictions are in effect and storage water is only used for necessary tasks such as drinking, cooking, and bathing.

* These assumptions are based on the following: 2.5 people per connection; 50 gallons/day per person.

* Source of supply offline but able to run booster pumps on some systems.

* In the event it becomes necessary to isolate or shut down any drinking water sources, drinking water may have to be provided through a state-certified water hauler, or by bottled water. Water conservation practices should be put into effect. The water system would coordinate with the Health Department to identify certified water haulers and shippers who would be contacted to provide water by truck.

Section 8.
Returning to Normal Operation

Returning to normal operations

| Action | Description and Actions |
| --- | --- |
| Inspect, flush, and disinfect the system | Operator and/or Assistant Operator to inspect all system facilities, to ensure all water quality tests have been done and the system has been flushed and disinfected if necessary. Operator makes a report to the Chairman. Operator’s decision on current condition of system. |
| Verify water quality | Operator verifies water quality sampling results. |
| Coordinate with local primacy agency | Operator coordinates with local primacy agency on system condition and water quality results |
| Notify customers | Clerk meets with operator to write notice to customers. Clerk directs communications to staff to distribute public notice |

Section 9.
Future Planning

Future Work to be done on Bayview’s water system.

In the month of May 2020 the community passed a bond issue of $3.4 million with a 1.75% interest rate on a 30 year long loan to refurbish the 1940 vintage system.

Project planned include refurbishing the 225,000 gallon Farragut storage tank (presently leased form the US Navy) along with installing a 12 inch water main throughout the town to increase pressure in the distribution system. Some modifications will be made to the pump house and associated piping to bring the two existing wells into today’s standards.

The final phase will concentrate on much needed repair of transmission lines that have leaking that amounts to about 118,000 gallons of drinking water daily.

These changes to the existing system should not affect the water source nor the discharge or pumping rates or the existing delineation area. However, a review of the present delineation areas of Well #7 and Well #8, will include a Potential Contaminant Inventory (PCI) of each of the two wells.

In the event that any new sources are added in the future, an updated Source Water Assessment (SWA) will be conducted on each source including potential contaminant inventories and risk assessment evaluation.

At that time, the town of Bayview will take appropriate actions to prevent the type of new development that may pose direct threats to the proposed new drinking water source(s). However, for the time being, the two current wells are more than adequate to serve the existing and possibly future needs of the community.

Section 10.
Plan Approval

Plan approval

This plan is officially in effect when reviewed, approved, and signed by the following people:

| Name/Title | Signature | Date |
| --- | --- | --- |
| Robert Kuchenski – Operator 208-683-3949 |  |  |
| Ali Spahn <alispahn@yahoo.com> |  |  |
| Faye & Ted Bare <bareted@live.com |  |  |
| Calvin Nolan <bullseyenid@yahoo.com> |  |  |
| Jessie Roe (district clerk) Bayview Water & Sewer District <bwsd637@gmail.com> |  |  |
| Larry Leake <larry.m.leake@hotmail.com> |  |  |
| Colleen Dahlseid <missionvlydoc@gmail.com> or <cdahl7bwsd@gmail.com> |  |  |
| Robert Hansen alternate operator 208-265-4270 |  |  |